| Purpose: | To document the framework for controlling the risks associated with electricity. Advise University staff, students and contractors of this framework. Detail particular responsibilities for electrical safety. |
| --- | --- |
| Policy/ Principles: Deans, Directors, Heads of Departments Testers of Electrical Equipment | The following have responsibilities for electrical safety: Implement the Electrical Safety policy which includes conducting risk assessments and where necessary the appointment of testing personnel to perform the testing requirements. Within an electrical testing program ensure that: - All plug-in type and fixed electrical equipment within a divisional or office area is inspected, tested, tagged and recorded in accordance with this policy and procedure. - All faulty electrical equipment is tagged appropriately and decommissioned from service until it satisfies the testing requirements. - Electrical equipment that has been tagged with a Danger/Out of Service Tag must not be used and must be removed from service until an appropriately licensed person has completed repairs. |
| Users of electrical equipment | - Only use University owned electrical equipment at the place of work. - Do not use any privately owned electrical equipment unless authorize by the Head of Department. - Note: Electrical inspection and testing of personal equipment is required to be tested as per Form 10a “Inspection and Testing of Electrical Equipment”. The cost for the inspection and testing of approved personal equipment is the responsibility of the Department. - Visually inspect all electrical equipment prior to use to check for obvious external damage, particularly to plugs, sockets, cords or other connectors. - Notify the appropriate supervisor of any faults and when equipment is out of service for maintenance or repair. - Always use an appropriate power board where more than one appliance is required to be connected to a single socket outlet - do not use double adaptors or “piggy-back” plugs. |
| Workgroup OHS Committee | Monitor and review the progress of the electrical safety program in the Division/Office |
| Scope: | All areas within the University in which electricity is used for work, teaching or research or associated activities. |
| Procedures: Person | Access to Electrical Switchboards Do not access University switchboards and do not reset any circuit breakers. Report tripped circuits to Office of Facilities Management – EXT 7150. |
| Competent person | Electrical Equipment Which Requires Testing and Tagging Not all electrical equipment is required to be tested. In some situations electrical equipment does not present a risk to the operator, due to: - • the permanent nature of their location; - • the way the equipment is used; - • the working environment in which the equipment is used. - Carry out a risk assessment in accordance with the risk management and consultation provisions (refer to OHS 3.00 – “Risk Management (Hazard Identification, Risk Assessment And Control” and WorkCover Guideline on Risk Assessments for Electrical Equipment). - Determine whether the electrical equipment requires testing and tagging as recommended in Form 10a “Inspection and Testing of Electrical Equipment” - Arrange for inspection and testing. Examples of equipment where electrical testing and tagging may be required due to cord flexion or connection activity include: Type of Equipment; Examples of Electrical Equipment. Hand held electrical equipment; • Hand held power tools, • Hairdryers, • Kitchen appliances, • Laboratory equipment. Portable electrical equipment moved while in operation; • Floor polishers, • Vacuum cleaners, • Portable lighting equipment. Electrical equipment that is moved between operations in such a manner that could damage the flexible supply lead; • Portable electronic whiteboards, • Overhead projectors, • Laptop computers, • Welding machines, • Extension cords, • Power boards. Electrical equipment that is used in a hostile working environment where damage to the equipment or the electricity supply to that equipment could occur such as in wet or dusty conditions.; • Electrical equipment used in wet or dusty areas, • Electrical equipment used outdoors, • In kitchens, • Laboratories (chemical damage), • Certain factory-type environments. Special circuit protection required for specified electrical equipment in workshops, laboratories, construction sites and other outdoor areas.; Residual current devices (RCDs). Note: Factors considered in determining appropriate inspection and test intervals include mobility of equipment, flexion of cord and the environment the equipment is used to evaluate risk to health and safety. The intervals in Form 10a are the minimum requirements for testing at the University. Additional tests may be undertaken to determine the safety of electrical equipment if it is felt necessary. This is at the discretion of the workplace supervisor in consultation with staff members. |
| Testers of Electrical Equipment Competent person | Fit an appropriate tag on electrical appliances that pass the inspection and testing procedure. The tag must include the identification number, the identity of the person carrying out the testing, the date tested and the date due for retest. Place a danger tag, warning persons of a potential hazard, on electrical appliances that do not pass the inspection and testing procedure. Withdrawn from service and quarantine equipment to ensure that it cannot be used. Arrange for repair of equipment through an authorised repair agents or suitably qualified electrical personnel. Re-test for compliance and then tagged accordingly prior to re-introduction to service. |
| Testers of Electrical Equipment | Record Keeping Keep records of inspection and testing of electrical equipment. Retain Inspection and testing records for the life of the equipment (Electronic testing records databases are acceptable). |
| Definitions: Competent Person Electrical Appliance Electrical Installation Extension Lead Fixed Equipment Socket Outlet Personal Equipment PAT Power Board RCD Tag Voltage | A person who has acquired through training, qualification, experience or a combination of these, the knowledge and skill to perform the task required correctly. A device or apparatus that is connected to the electrical power supply through a general purpose outlet in the form of a plug-in type. A system that supplies electricity to a building, including the switchboards, distribution boards, fixed wiring and socket outlets. An assembly of a plug intended for connection to a mains outlet socket, a sheathed flexible cord and a cord extension socket. Equipment that is fastened to a support, secured in position or otherwise due to its size and mass located in a specific location. A three-pin wall socket that delivers 240 volts Any privately owned electrical equipment of the plug-in type to be used at the University. Examples of personal equipment include (but is not limited to) radios, electric heaters and fans, sandwich makers, coffee makers, and mobile phones. A Portable Appliance Tester is an electronic instrument that automatically tests equipment plugged into it. The results it indicates require no technical interpretation. A device having a single plug intended for connection to a mains outlet socket, a sheathed flexible cord and an assembly of one or more outlet sockets. A Residual Current Device is a mechanical switching device intended to isolate the circuit when the current imbalance attains the rated operating leakage current value of the device. A durable, non-reusable, non-metallic label that may be colour coded to identify the period in which testing was performed. The difference in electrical potential between two points in a circuit, normally existing between conductors and between conductors and earth, expressed in volts. |
| Forms: | - Form 10a “Inspection and Testing of Electrical Equipment” Form 2c “Safety Checklist – Electrical” |
| References: | Occupational Health and Safety Act 2000 Occupational Health and Safety Amendment (Electrical Equipment) Regulation 2006 OHS 3.00 – “Risk Management (Hazard Identification, Risk Assessment And Control)” WorkCover Guideline on Risk Assessments for Electrical Equipment AS/NZS 3760 |

| Source/Contact: Manager, Occupational Health and Safety | Process Owner/Publisher: Occupational Health and Safety |
| --- | --- |
| Created: July 2006 | Status: Issued |